SECTION 12345

SHORT-CIRCUIT/COORDINATION STUDY/arc flash RISK ASSESSMENT

GENERAL

SCOPE

The contractor shall furnish short-circuit and protective device coordination studies as prepared by the electrical equipment manufacturer or an approved engineering firm.

The contractor shall furnish an Arc Flash Risk Assessment Study per the requirements set forth in NFPA 70E - Standard for Electrical Safety in the Workplace.  The arc flash risk assessment shall be performed according to the IEEE 1584 equations that are presented in NFPA70E, Annex D.

The scope of the studies shall include all new distribution equipment supplied by the equipment Manufacturer under this contract.  - OR - The scope of the studies shall include all new distribution equipment supplied by the equipment Manufacturer under this contract as well as all directly affected existing distribution equipment at the customer facility.  - OR -  The scope of the studies shall include all new distribution equipment supplied by the equipment Manufacturer under this contract as well as all existing distribution equipment at the customer facility.

related sections

references

Institute of Electrical and Electronics Engineers, Inc. (IEEE):

IEEE 141 – Recommended Practice for Electric Power Distribution and Coordination of Industrial and Commercial Power Systems

IEEE 242 – Recommended Practice for Protection and Coordination of Industrial and Commercial Power Systems

IEEE 399 – Recommended Practice for Industrial and Commercial Power System Analysis

IEEE 241 – Recommended Practice for Electric Power Systems in Commercial Buildings

IEEE 1015 – Recommended Practice for Applying Low-Voltage Circuit Breakers Used in Industrial and Commercial Power Systems.

IEEE 1584 - Guide for Performing Arc-Flash Hazard Calculations

American National Standards Institute (ANSI):

ANSI C57.12.00 – Standard General Requirements for Liquid-Immersed Distribution, Power, and Regulating Transformers

ANSI C37.13 – Standard for Low Voltage AC Power Circuit Breakers Used in Enclosures

ANSI C37.010 – Standard Application Guide for AC High Voltage Circuit Breakers Rated on a Symmetrical Current Basis

ANSI C 37.41 – Standard Design Tests for High Voltage Fuses, Distribution Enclosed Single-Pole Air Switches, Fuse Disconnecting Switches and Accessories.

The National Fire Protection Association (NFPA)

NFPA 70 - National Electrical Code, latest edition

NFPA 70E – Standard for Electrical Safety in the Workplace

submittals for review/approval

The short-circuit and protective device coordination studies shall be submitted to the design engineer prior to receiving final approval of the distribution equipment shop drawings and/or prior to release of equipment drawings for manufacturing. If formal completion of the studies may cause delay in equipment manufacturing, approval from the engineer may be obtained for preliminary submittal of sufficient study data to ensure that the selection of device and characteristics will be satisfactory.

submittals for construction

The results of the short-circuit, protective device coordination and arc flash risk assessment studies shall be summarized in a final report. No more than five (5) bound copies of the complete final report shall be submitted. For large system studies, submittals requiring more than five (5) copies of the report will be provided without the section containing the computer printout of the short-circuit input and output data.  Additional copies of the short-circuit input and output data, where required, shall be provided on CD in PDF format.

Following best practices, the contractor is to provide the study project files to the Owner in electronic format to allow the Owner to review all aspects of the project input data and reprint arc flash labels, one-line diagrams, reports etc. The electronic project files are critical for disaster recovery and maintaining the power system.  In addition, a copy the PTW Viewer program is required to accompany the electronic project files (or Owner to purchase directly from SKM).

The report shall include the following sections:

Executive Summary.

Descriptions, purpose, basis and scope of the study

Tabulations of circuit breaker, fuse and other protective device ratings versus calculated short circuit duties

Protective device time versus current coordination curves, tabulations of relay and circuit breaker trip unit settings, fuse selection

Fault current calculations including a definition of terms and guide for interpretation of the computer printout

Details of the incident energy and flash protection boundary calculations

Recommendations for system improvements, where needed

One-line diagram

Arc flash labels shall be provided in hard copy only. -OR- Arc flash labels shall be provided in hard copy and for large system studies with more than 200 bus locations, a copy of the computer analysis software viewer program is required to provide arc flash labels in electronic format.

qualifications

The short-circuit, protective device coordination and arc flash risk assessment studies shall be conducted under the supervision and approval of a Registered/Licensed Professional Electrical Engineer skilled in performing and interpreting the power system studies.

The Registered/Licensed Professional Electrical Engineer shall be a full-time employee of the equipment manufacturer or an approved engineering firm

The Registered/Licensed Professional Electrical Engineer shall have a minimum of five (5) years of experience in performing power system studies.

The equipment manufacturer or approved engineering firm shall demonstrate experience with Arc Flash Risk Assessment by submitting names of at least ten actual arc flash risk assessment it has performed in the past year.

Computer Analysis Software

The studies shall be performed using the latest revision of the SKM Systems Analysis Power*Tools for Windows (PTW) software program or approved equal.

product

studies

Contractor to furnish short-circuit and protective device coordination studies as prepared by equipment manufacturer or an approved engineering firm.

The contractor shall furnish an Arc Flash Risk Assessment Study per NFPA 70E - Standard for Electrical Safety in the Workplace, reference Article 130.5 and Annex D.

Data collection

Contractor shall furnish all data as required by the power system studies. The Engineer performing the short-circuit, protective device coordination and arc flash risk assessment studies shall furnish the Contractor with a listing of required data immediately after award of the contract. The Contractor shall expedite collection of the data to assure completion of the studies as required for final approval of the distribution equipment shop drawings and/or prior to the release of the equipment for manufacturing.

Source combination may include present and future motors and generators.

Load data utilized may include existing and proposed loads obtained from Contract Documents provided by Owner, or Contractor.

If applicable, include fault contribution of existing motors in the study. The Contractor shall obtain required existing equipment data, if necessary, to satisfy the study requirements.

short-circuit and protective device evaluation study

Use actual conductor impedances if known.  If unknown, use typical conductor impedances based on IEEE Standard 141-1993.

Transformer design impedances shall be used when test impedances are not available.

Provide the following:

Calculation methods and assumptions

Selected base per unit quantities

One-line diagram of the system being evaluated

Source impedance data, including electric utility system and motor fault contribution characteristics

Tabulations of calculated quantities

Results, conclusions, and recommendations.

Calculate short-circuit momentary and interrupting duties for a three-phase bolted fault 
at each:

Electric utility’s supply termination point

Incoming switchgear

Unit substation primary and secondary terminals

Low voltage switchgear

Motor control centers

Standby generators and automatic transfer switches

Branch circuit panelboards

Other significant locations throughout the system.

For grounded systems, provide a bolted line-to-ground fault current study for areas as defined for the three-phase bolted fault short-circuit study.

Protective Device Evaluation:

Evaluate equipment and protective devices and compare to short circuit ratings

Adequacy of switchgear, motor control centers, and panelboard bus bars to withstand short-circuit stresses

Notify Owner in writing, of existing, circuit protective devices improperly rated for the calculated available fault current.

protective device coordination study

Proposed protective device coordination time-current curves (TCC) shall be displayed on log-log scale graphs.

Include on each TCC graph, a complete title and one-line diagram with legend identifying the specific portion of the system covered.

Terminate device characteristic curves at a point reflecting maximum symmetrical or asymmetrical fault current to which the device is exposed.

Identify the device associated with each curve by manufacturer type, function, and, if applicable, tap, time delay, and instantaneous settings recommended.

Plot the following characteristics on the TCC graphs, where applicable:

Electric utility’s overcurrent protective device

Medium voltage equipment overcurrent relays

Medium and low voltage fuses including manufacturer’s minimum melt, total clearing, tolerance, and damage bands

Low voltage equipment circuit breaker trip devices, including manufacturer’s tolerance bands

Transformer full-load current, magnetizing inrush current, and ANSI through-fault protection curves

Conductor damage curves

Ground fault protective devices, as applicable

Pertinent motor starting characteristics and motor damage points, where applicable

Pertinent generator short-circuit decrement curve and generator damage point

The largest feeder circuit breaker in each motor control center and applicable panelboard.

Provide adequate time margins between device characteristics such that selective operation is provided, while providing proper protection.

Arc Flash RISK ASSESSMENT

The arc flash risk assessment shall be performed according to the IEEE 1584 equations that are presented in NFPA70E, Annex D.

The flash protection boundary and the incident energy shall be calculated at all significant locations in the electrical distribution system (switchboards, switchgear, motor-control centers, panelboards, busway and splitters) where work could be performed on energized parts.

The Arc-Flash Risk Assessment shall include all significant locations in 240 volt and 208 volt systems fed from transformers equal to or greater than 125 kVA where work could be performed on energized parts.

Safe working distances shall be based upon the calculated arc flash boundary considering an incident energy of 1.2 cal/cm2.

When appropriate, the short circuit calculations and the clearing times of the phase overcurrent devices will be retrieved from the short-circuit and coordination study model.  Ground overcurrent relays should not be taken into consideration when determining the clearing time when performing incident energy calculations

The short-circuit calculations and the corresponding incident energy calculations for multiple system scenarios must be compared and the greatest incident energy must be uniquely reported for each equipment location.  Calculations must be performed to represent the maximum and minimum contributions of fault current magnitude for all normal and emergency operating conditions. The minimum calculation will assume that the utility contribution is at a minimum and will assume a minimum motor contribution (all motors off). Conversely, the maximum calculation will assume a maximum contribution from the utility and will assume the maximum amount of motors to be operating.  Calculations shall take into consideration the parallel operation of synchronous generators with the electric utility, where applicable.

The incident energy calculations must consider the accumulation of energy over time when performing arc flash calculations on buses with multiple sources. Iterative calculations must take into account the changing current contributions, as the sources are interrupted or decremented with time.  Fault contribution from motors and generators should be decremented as follows:

Fault contribution from induction motors should not be considered beyond 3-5 cycles.

Fault contribution from synchronous motors and generators should be decayed to match the actual decrement of each as closely as possible (e.g. contributions from permanent magnet generators will typically decay from 10 per unit to 3 per unit after 10 cycles).

For each equipment location with a separately enclosed main device (where there is adequate separation between the line side terminals of the main protective device and the work location), calculations for incident energy and flash protection boundary shall include both the line and load side of the main breaker.

When performing incident energy calculations on the line side of a main breaker (as required per above), the line side and load side contributions must be included in the fault calculation.

Mis-coordination should be checked amongst all devices within the branch containing the immediate protective device upstream of the calculation location and the calculation should utilize the fastest device to compute the incident energy for the corresponding location.

Arc Flash calculations shall be based on actual overcurrent protective device clearing time. Maximum clearing time will be capped at 2 seconds based on IEEE 1584-2002 section B.1.2.  Where it is not physically possible to move outside of the flash protection boundary in less than 2 seconds during an arc flash event, a maximum clearing time based on the specific location shall be utilized.

report sections

Input data shall include, but not be limited to the following:

Feeder input data including feeder type (cable or bus), size, length, number per phase, conduit type (magnetic or non-magnetic) and conductor material (copper or aluminum).

Transformer input data, including winding connections, secondary neutral-ground connection, primary and secondary voltage ratings, kVA rating, impedance, % taps and phase shift.

Reactor data, including voltage rating, and impedance.

Generation contribution data, (synchronous generators and Utility), including short-circuit reactance (X”d), rated MVA, rated voltage, three-phase and single line-ground contribution (for Utility sources) and X/R ratio.

Motor contribution data (induction motors and synchronous motors), including short-circuit reactance, rated horsepower or kVA, rated voltage, and X/R ratio.

Short-Circuit Output Data shall include, but not be limited to the following reports:

Low Voltage Fault Report shall include a section for three-phase and unbalanced fault calculations and shall show the following information for each applicable location:

Voltage

Calculated fault current magnitude and angle

Fault point X/R ratio

Equivalent impedance

Momentary Duty Report shall include a section for three-phase and unbalanced fault calculations and shall show the following information for each applicable location:

Voltage

Calculated symmetrical fault current magnitude and angle

Fault point X/R ratio

Calculated asymmetrical fault currents

Based on fault point X/R ratio

Based on calculated symmetrical value multiplied by 1.6

Based on calculated symmetrical value multiplied by 2.7

Equivalent impedance

Interrupting Duty Report shall include a section for three-phase and unbalanced fault calculations and shall show the following information for each applicable location:

Voltage

Calculated symmetrical fault current magnitude and angle

Fault point X/R ratio

No AC Decrement (NACD) Ratio

Equivalent impedance

Multiplying factors for 2, 3, 5 and 8 cycle circuit breakers rated on a symmetrical basis

Multiplying factors for 2, 3, 5 and 8 cycle circuit breakers rated on a total basis

Recommended Protective Device Settings:

Phase and Ground Relays:

Current transformer ratio

Current setting

Time setting

Instantaneous setting

Recommendations on improved relaying systems, if applicable.

Circuit Breakers:

Adjustable pickups and time delays (long time, short time, ground)

Adjustable time-current characteristic

Adjustable instantaneous pickup

Recommendations on improved trip systems, if applicable.

Incident energy and flash protection boundary calculations

Arcing fault magnitude

Protective device clearing time

Duration of arc

Arc flash boundary

Working distance

Incident energy

Hazard Risk Category*

Recommendations for arc flash energy reduction

*Applicable only when using the arc flash PPE category method.

EXECUTION

field adjustment

Adjust relay and protective device settings according to the recommended settings table provided by the coordination study. Field adjustments to be completed by the engineering service division of the equipment manufacturer under the Startup and Acceptance Testing contract portion.

Make minor modifications to equipment as required to accomplish conformance with short circuit and protective device coordination studies.

Notify Owner in writing of any required major equipment modifications.

ARC FLASH WARNING LABELs

The contractor of the Arc Flash Risk Assessment shall provide a 3.5 in. x 5 in. thermal transfer type label of high adhesion polyester for each work location analyzed.

All labels will be based on recommended overcurrent device settings and will be provided after the results of the analysis have been presented to the owner and after any system changes, upgrades or modifications have been incorporated in the system.

The label shall include the following information, at a minimum:

Location designation

Nominal voltage

Flash protection boundary

Hazard risk category*

Incident energy

Working distance

Engineering report number, revision number and issue date.

*Applicable only when using the arc flash PPE category method.

Labels shall be machine printed, with no field markings.

Arc flash labels shall be provided in the following manner and all labels shall be based on recommended overcurrent device settings.

For each 600, 480 and applicable 208 volt panelboard, one arc flash label shall be provided.

For each motor control center, one arc flash label shall be provided.

For each low voltage switchboard, one arc flash label shall be provided.

For each switchgear, one flash label shall be provided.

For medium voltage switches one arc flash label shall be provided

Labels shall be field installed by the engineering service division of the equipment manufacturer under the Startup and Acceptance Testing contract portion.

ARC FLASH TRAINING

The contractor of the Arc Flash Risk Assessment shall train the owner’s qualified electrical personnel of the potential arc flash risks associated with working on energized equipment  (minimum of 4 hours).